Reverse Osmosis Plant for the Production of Pure Water—Instructions for Operators
The following instructions give a step-by-step guide of how to operate the plant, and what is expected to happen at each stage. Reference to tag numbers can be found on the P&ID and all parts are tagged on the plant.
# Installation
1. Connect a water supply to the bottom of flow meter FI25.
2. Connect the RO water output to the site storage tank. Connection is just downstream of SV04.
3. Connect the level indication cable to the level transmitter installed on your site storage tank. This level transmitter needs to provide a 4-20mA signal depending on the RO water level in the storage tank.
4. Note that the waste drain from FI31 discharges continuously during production. This may require connection to your drains.
5. Connect 5-wire 3-phase power supply to the plug.
6. Fill metabisulphite tank with 10% solution.
# Producing Pure Water
Ensure the manual valves are in their correct positions:
  - MV01, which drains the feed tank, should be closed.
  - MV02, which drains the permeate tank, should be closed.
  - MV04, which controls the proportion of water sent to waste, should be closed.
  - MV05, which limits flow returning to the feed tank and thus controls the inlet pressure to the membranes, should be fully open.
  - MV06, which isolates supply to the first of the two membranes, should be open.
  - MV07, which isolates supply to the second of the two membranes, should be open.
  - MV08, which isolates retentate output from the first of the two membranes, should be open.
  - MV09, which isolates retentate output from the second of the two membranes, should be open.
  - MV10, which isolates permeate output from the first of the two membranes, should be open.
  - MV11, which isolates permeate output from the second of the two membranes, should be open.
1. To begin operation, turn the main switch from OFF to PRODUCT.
2. Raw process water will enter through control valve SV02. The chemical pump, PP02, will start up and pump sodium metabisulphiote into the water stream going to the feed tank, TK11. Sodium metabisulphite removes the chlorine from the water before it is passed through the membranes.
3. Feed tank TK11 will fill with water.
4. When the tank is full, pump PP02 will stop running and the isolation valve SV02 will close.
5. The main pump, PP03, will start up.
6. Water will be pumped from the feed tank, TK11, through the membranes, until the plant has accumulated three minutes of run time where the conductivity meter was below a specified threshold. Some of the water will return to tank TK11 and the rest will go to drain. During these three minutes:
  - valve MV04, which controls the rate of water that is sent to drain, should be opened somewhat. It should be opened such that the ratio of permeate flow to waste flow is no more than 2:1 (that is, 67% recovery, 33% to drain).
  - valve MV05, which limits flow returning to the feed tank and thus effectively controls the inlet pressure at the membranes, should be closed somewhat from its fully open position. Closing this valve will increasing the pressure at the membranes and thus increase permeate flow. The following should be kept in mind:
    - permeate flow at FI26 should be a minimum of 700 L/h, any less and the system needs to be cleaned.
    - the membrane inlet pressure must stay below 23 barg. This threshold is marked in black on the pressure guage.
    - the pressure differential along the membranes (as measured by dPI15) should be below 0.7barg. This threshold is marked in black on the pressure guage.
    - changing the position of MV05 may require that MV04 is also adjusted.
1. Once the permeate tank TK32 is full, good RO water will flow into the site storage tank(s). Pump PP03 will increase speed to 100%.
2. As the level in the storage tanks rises, pump PP03 will reduce speed.
# Controlled Shutdown
When the site tank(s) fill completely, or if the main switch is changed to the OFF position, the system will begin a controlled shutdown:
1. The permeate tank TK32 will discharge clean RO water through the membranes and then to drain.
2. Once the membranes are rinsed, the system will shut off. Tank TK32 will be about half full after this process.
# Unplanned Shutdowns
The system may begin to shut down suddenly, even if the process is not complete. It will either perform a controlled shutdown as above, or an emergency shutdown. In an emergency shutdown, everything will immediately stop and turn off.
- An unplanned, but controlled, shutdown may occur because:
  - the level in tank the permeate tank TK32 may be low.
  - the conductivity may have been too high for an extended period of time (say, 15 minutes).
- An emergency shutdown may occur because:
  - an electrical fault is detected.
  - “Emergency Shutdown” is initiated by the operator turning the power off.
  - the level in the feed tank TK11 is critically low.
# Operating Conditions
The following instruments need to be monitored. The process has certain minimum/maximum operating specifications as follows:
- Filter differential pressure P1 – P2 < 0.2 barg. If this condition is not met then the filter cartridges need to be replaced. Either 1 or 5 micron cartridges are recommended.
- Pump pressure: PI14 < 23 barg
- Membrane retentate differential pressure: dPI15 < 0.7 barg
- Ratio of flows FI26:FI31 should be no more than 2:1 (that is, 67% recovery, 33% to drain)
- Permeate flow FI26 should be a minimum of 700 L/h, any less and the system needs to be cleaned.
- Metabisulfite should be pumped at a rate of 15ml per 1000L of inlet water. Thus, if FI25 indicates you are running at 2000L/h then the pump PP02 should be set to run at 30ml/h. The current setting is displayed on the pump screen and can easily be changed by pressing the left or right arrows to decrease or increase the flow rate.
# Cleaning
A thorough cleaning of the membranes should be performed approximately once a month. Details of the procedure are as follows:
1. Ensure the Recirc switch is in the OFF position.
2. Set the main switch to PRODUCT. Wait until water is being sent to the site storage via SV04.
3. Set the main switch to the OFF position to begin a controlled shutdown and immediately close MV04 to ensure that water is not going to drain during the shutdown.
4. Once the plant has shutdown, tank TK32 should be about half full. Switch the main switch to FLUSH and the recirc switch to NO FILL. Water will now be circulating from TK11, through the membranes, and back to TK11. No water should be going to drain. Tank TK11 will be about three-quarters full.
5. Add approximately 1L of Ultrasil 91 to tank TK11. This should give a pH of around 10.5-11.0.
6. Leave the plant running for 30 minutes. Periodically check the pH and add more Ultrasil 91 if the pH falls below 10.
7. Drain TK11 using MV01.
8. Close MV01 and set the Recirc switch to FILL.
9. Once tank TK11 is full, the system will begin flushing again. Test the pH during this flush. If it is significantly higher than 7.0 then repeat steps 6-8 until the pH is acceptable.
10. Repeat steps 2-4. As you begin the product cycle, restore MV04 to its open position at half of the inlet flow rate.
11. Add approximately 1L of Ultrasil 75. This should give a pH of around 2.5-3.0.
12. Leave the plant running for 30 minutes, again adding Ultrasil 75 if the pH goes above 3.5.
13. Drain TK11 using MV01.
14. Close MV01 and set the Recirc switch to FILL
15. Once tank TK11 is full, the system will begin flushing again. Test the pH during this flush. If it is significantly less than 7.0, repeat steps 12-14 until pH is acceptable.
# Fault
If the fault light is illuminated, this indicates that the RO water conductivity is unacceptable. Only when the RO water has passed the conductivity test continually for three minutes will the RO water be sent to the product tank. Consider cleaning or replacing the membranes if the fault light remains lit.